## Renewable Capacity ISP
Renewable Energy Capacity
This sheet contains information relating to the forecast amount of renewable capacity that is expected in SA under the step change scenario over the forecast period.
The data included here is for wind and solar. Note that this solar is "Utility Scale Solar" meaning that it is not inclusive of residential and business rooftop PV.
The wind and solar data are inclusive of both exisiting capacities and those projects that are committed but also forecasted amounts that are expected to be developed under the step change scenario.
Historic figures from SAER. Note that historic figures are in nameplate capacity whereas future is in typical summer rating in MW. This explains the slight difference. Also, AEMO doesn't count ADP 2 in assumptions but counts it in SAER.
Capacity GW
FY | Wind | Solar
2018-19 | 2.141 | 0.378
2019-20 | 2.141 | 0.378
2020-21 | 2.141 | 0.411 |  | Goyder A | 200.982 | 0.20098
2021-22 | 2.351 | 0.488 |  | Goyder B | 137.011 | 0.13701
2022-23 | 2.348 | 0.661
2023-24 | 2.2525 | 0.60913 | 8.8564 | 3.7455
2024-25 | 2.5904 | 0.60912
2025-26 | 2.7306 | 0.60912
2026-27 | 2.8022 | 0.88888
2027-28 | 3.0073 | 0.88888
2028-29 | 3.1605 | 0.88888
2029-30 | 4.127 | 0.88888
2030-31 | 4.1022 | 1.4046
2031-32 | 4.1022 | 1.3984
2032-33 | 4.3442 | 1.3984
2033-34 | 4.4897 | 1.3984
2034-35 | 4.5339 | 1.3984
2035-36 | 4.3868 | 1.3984
2036-37 | 4.2023 | 1.6133
2037-38 | 4.2023 | 1.6133
2038-39 | 4.0433 | 1.6133
2039-40 | 3.7166 | 1.6133
2040-41 | 4.1863 | 2.4378
2041-42 | 4.1863 | 2.3639
2042-43 | 4.4774 | 2.401
2043-44 | 4.2904 | 3.0058
2044-45 | 4.2904 | 5.3947
2045-46 | 5.1947 | 5.3761
2046-47 | 5.3116 | 5.3761
2047-48 | 5.3116 | 5.2969
2048-49 | 5.7079 | 5.2969
2049-50 | 5.5123 | 5.2019
2050-51 | 5.5123 | 5.2059
2051-52 | 5.5123 | 5.2059

## Average CF
Average Capacity Factor of Solar and Wind Traces
For illustration purposes, the capactiy factor for solar and wind traces within SA were calculated.
FY | Solar | Wind Medium | Wind High
2024-25 | 0.26988 | 0.38154 | 0.38154 | 2025 | 0.26988 | 0.38154 | 0.38154
2025-26 | 0.28224 | 0.36852 | 0.36852 | 2026 | 0.28224 | 0.36852 | 0.36852
2026-27 | 0.26796 | 0.34817 | 0.35196 | 2027 | 0.26796 | 0.34817 | 0.35196
2027-28 | 0.26877 | 0.36704 | 0.37355 | 2028 | 0.26877 | 0.36704 | 0.37355
2028-29 | 0.26516 | 0.35539 | 0.36261 | 2029 | 0.26516 | 0.35539 | 0.36261
2029-30 | 0.26639 | 0.34202 | 0.34848 | 2030 | 0.26639 | 0.34202 | 0.34848
2030-31 | 0.2435 | 0.33034 | 0.33641 | 2031 | 0.2435 | 0.33034 | 0.33641
2031-32 | 0.26101 | 0.3565 | 0.36347 | 2032 | 0.26101 | 0.3565 | 0.36347
2032-33 | 0.27297 | 0.35565 | 0.36214 | 2033 | 0.27297 | 0.35565 | 0.36214
2033-34 | 0.26387 | 0.38734 | 0.39568 | 2034 | 0.26387 | 0.38734 | 0.39568
2034-35 | 0.27195 | 0.34399 | 0.35217 | 2035 | 0.27195 | 0.34399 | 0.35217
2035-36 | 0.26893 | 0.35388 | 0.36101 | 2036 | 0.26893 | 0.35388 | 0.36101
2036-37 | 0.27843 | 0.3442 | 0.3519 | 2037 | 0.27843 | 0.3442 | 0.3519
2037-38 | 0.28317 | 0.38415 | 0.39339 | 2038 | 0.28317 | 0.38415 | 0.39339
2038-39 | 0.29155 | 0.38722 | 0.39544 | 2039 | 0.29155 | 0.38722 | 0.39544
2039-40 | 0.30012 | 0.37275 | 0.38347 | 2040 | 0.30012 | 0.37275 | 0.38347
2040-41 | 0.28454 | 0.35883 | 0.36917 | 2041 | 0.28454 | 0.35883 | 0.36917
2041-42 | 0.28317 | 0.37662 | 0.38971 | 2042 | 0.28317 | 0.37662 | 0.38971
2042-43 | 0.27801 | 0.36699 | 0.38047 | 2043 | 0.27801 | 0.36699 | 0.38047
2043-44 | 0.2813 | 0.34106 | 0.35314 | 2044 | 0.2813 | 0.34106 | 0.35314
2044-45 | 0.25195 | 0.33023 | 0.34093 | 2045 | 0.25195 | 0.33023 | 0.34093
2045-46 | 0.26857 | 0.3539 | 0.3693 | 2046 | 0.26857 | 0.3539 | 0.3693
2046-47 | 0.28031 | 0.34823 | 0.36255 | 2047 | 0.28031 | 0.34823 | 0.36255
2047-48 | 0.27272 | 0.3794 | 0.3973 | 2048 | 0.27272 | 0.3794 | 0.3973
2048-49 | 0.28346 | 0.33536 | 0.35232 | 2049 | 0.28346 | 0.33536 | 0.35232
2049-50 | 0.28052 | 0.35049 | 0.36166 | 2050 | 0.28052 | 0.35049 | 0.36166
2050-51 | 0.28093 | 0.34205 | 0.35629 | 2051 | 0.28093 | 0.34205 | 0.35629
2051-52 | 0.28345 | 0.38122 | 0.39847 | 2052 | 0.28345 | 0.38122 | 0.39847

## Renewable Generation ISP
Renewable Energy Generation ISP
This sheet contains information relating to the forecast amount of annual renewable generation that is expected in SA under the step change scenario over the forecast period.
The data included here is for wind and solar. Note that this solar is "Utility Scale Solar" meaning that it is not inclusive of residential and business rooftop PV.
The annual generation amounts are based on reference years for each of the existing sites and REZs. This, therefore, captures, to an extent, the short and medium term nature of wind and solar.
Historic data is from the SAER.
Annual Generation TWh
FY | Wind Medium | Wind High | Solar
2018-19 | 5.724 | 5.724 | 0.30291
2019-20 | 5.797 | 5.797 | 0.48329
2020-21 | 5.738 | 5.738 | 0.67281
2021-22 | 6.131 | 6.131 | 0.69811
2022-23 | 6.6514 | 6.6514 | 0.80444
2023-24 | #N/A | #N/A | #N/A
2024-25 | 8.6442 | 8.6442 | 1.44
2025-26 | 8.8103 | 8.8103 | 1.4722
2026-27 | 8.5415 | 8.5527 | 2.0865
2027-28 | 9.6874 | 9.7613 | 2.0985
2028-29 | 9.85 | 9.9515 | 2.0647
2029-30 | 12.3075 | 12.5653 | 2.0743
2030-31 | 11.8858 | 12.1125 | 3.0932
2031-32 | 12.8155 | 13.0551 | 3.3014
2032-33 | 13.5484 | 13.798 | 3.4493
2033-34 | 15.1672 | 15.5554 | 3.3596
2034-35 | 13.5933 | 13.9514 | 3.4407
2035-36 | 13.6794 | 13.914 | 3.4033
2036-37 | 12.667 | 12.957 | 3.9416
2037-38 | 14.2344 | 14.5924 | 4.0123
2038-39 | 13.7315 | 14.0211 | 4.1344
2039-40 | 12.1022 | 12.4537 | 4.26
2040-41 | 13.1233 | 13.5591 | 6.0483
2041-42 | 13.6902 | 14.2704 | 5.8389
2042-43 | 14.3584 | 14.9835 | 5.8774
2043-44 | 12.7758 | 13.2853 | 7.4504
2044-45 | 12.4002 | 12.8364 | 11.9496
2045-46 | 16.1219 | 16.8053 | 12.656
2046-47 | 16.2156 | 16.8665 | 13.2008
2047-48 | 17.7247 | 18.5396 | 12.6311
2048-49 | 16.7696 | 17.614 | 13.1387
2049-50 | 16.9278 | 17.4653 | 12.7615
2050-51 | 16.5232 | 17.2061 | 12.7855
2051-52 | 18.4608 | 19.29 | 12.9315

## Demand by Category
Demand by Category
This sheet contains information relating to the forecast demand in SA under the step change scenario over the forecast period. The annual demand amount, by category, is shown below.
The categories are as given below. Demand is given as "Operational Demand" which is the demand after rooftop PV, small non-scheduled generation and energy efficiency gains have been removed.
This demand is named OPSO_MODELLING which is equal to OPSO - ICL + EVVPP. This is the version that AEMO uses in their modelling. However, this does not include hydrogen demand.
Hydrogen demand has been added separately to the OPSO_MODELLING evenly to each half hour period. These numbers are also 10POE, meaning there is a 10% likelihood under the step change scenario that these are exceeded.
Demand (TWh)
FY | Business | EVs | Electrification | Hydrogen | Residential | Losses | Operational Demand | Actual Operational Demand
2018-19 | [7 empty] | 12.2365
2019-20 | [7 empty] | 11.9636
2020-21 | [7 empty] | 11.616
2021-22 | [7 empty] | 11.4475
2022-23 | [7 empty] | 11.5063
2023-24 | [7 empty] | N/A
2024-25 | 8.383 | 0.035619 | 0.10685 | 0.0089194 | 1.9447 | 0.89863 | 11.3777
2025-26 | 8.4712 | 0.08056 | 0.32371 | 0.39813 | 1.8064 | 0.92317 | 12.0032
2026-27 | 8.6399 | 0.15631 | 0.62698 | 1.1501 | 1.6616 | 0.95824 | 13.1931
2027-28 | 8.8648 | 0.26142 | 0.90923 | 1.5493 | 1.4883 | 0.99144 | 14.0646
2028-29 | 8.7836 | 0.39671 | 1.2048 | 1.887 | 1.2918 | 1.0144 | 14.5782
2029-30 | 8.7642 | 0.56495 | 1.4118 | 2.318 | 1.1163 | 1.0392 | 15.2144
2030-31 | 8.7403 | 0.75537 | 1.6384 | 3.0569 | 0.97112 | 1.0708 | 16.2328
2031-32 | 8.7373 | 0.96285 | 1.7129 | 3.1786 | 0.83948 | 1.0914 | 16.5226
2032-33 | 8.7254 | 1.1931 | 1.7541 | 3.1466 | 0.7204 | 1.1108 | 16.6503
2033-34 | 8.7395 | 1.4467 | 1.8348 | 3.5399 | 0.61669 | 1.1402 | 17.3178
2034-35 | 8.7416 | 1.6989 | 2.062 | 2.75 | 0.51893 | 1.1825 | 16.9539
2035-36 | 8.7456 | 1.9642 | 2.3521 | 3.0027 | 0.42992 | 1.233 | 17.7275
2036-37 | 8.7612 | 2.2166 | 2.6691 | 3.2816 | 0.35362 | 1.2867 | 18.5688
2037-38 | 8.7915 | 2.4764 | 2.8397 | 3.7948 | 0.28113 | 1.3276 | 19.5112
2038-39 | 8.751 | 2.7359 | 2.9969 | 3.61 | 0.19578 | 1.3634 | 19.653
2039-40 | 8.645 | 3.0076 | 3.0954 | 3.9107 | 0.12929 | 1.3906 | 20.1787
2040-41 | 8.5398 | 3.2579 | 3.2697 | 3.8827 | 0.053336 | 1.4211 | 20.4246
2041-42 | 8.4416 | 3.5184 | 3.4358 | 4.8261 | -0.010369 | 1.4542 | 21.6657
2042-43 | 8.3587 | 3.7803 | 3.5864 | 4.5685 | -0.078031 | 1.4867 | 21.7027
2043-44 | 8.2508 | 4.0556 | 3.6697 | 4.8655 | -0.15147 | 1.5108 | 22.2009
2044-45 | 8.1029 | 4.3038 | 3.7297 | 5.0036 | -0.22177 | 1.5226 | 22.4408
2045-46 | 7.9196 | 4.5669 | 3.7221 | 4.7766 | -0.32089 | 1.5247 | 22.1891
2046-47 | 7.722 | 4.83 | 3.6447 | 4.8338 | -0.42449 | 1.5177 | 22.1237
2047-48 | 7.5698 | 5.1115 | 3.5797 | 4.8648 | -0.52478 | 1.5198 | 22.1208
2048-49 | 7.4182 | 5.3555 | 3.4802 | 5.5497 | -0.6181 | 1.5137 | 22.6991
2049-50 | 7.2768 | 5.5929 | 3.4426 | 5.5757 | -0.67338 | 1.5194 | 22.734
2050-51 | 7.1413 | 5.7145 | 3.3831 | 5.6938 | -0.7319 | 1.5104 | 22.7112
2051-52 | 6.9875 | 5.7707 | 3.3881 | 5.836 | -0.78978 | 1.501 | 22.6935
FY | Business | EVs | Electrification | Hydrogen | Residential | Losses | Operational Demand
2024-25 | 73.68% | 0.3131% | 0.9391% | 0.07839% | 17.09% | 7.898% | 1
2025-26 | 70.57% | 0.6712% | 2.697% | 3.317% | 15.05% | 7.691% | 1
2026-27 | 65.49% | 1.185% | 4.752% | 8.718% | 12.59% | 7.263% | 1
2027-28 | 63.03% | 1.859% | 6.465% | 11.02% | 10.58% | 7.049% | 1
2028-29 | 60.25% | 2.721% | 8.264% | 12.94% | 8.861% | 6.958% | 1
2029-30 | 57.6% | 3.713% | 9.279% | 15.24% | 7.337% | 6.83% | 1
2030-31 | 53.84% | 4.653% | 10.09% | 18.83% | 5.982% | 6.597% | 1
2031-32 | 52.88% | 5.827% | 10.37% | 19.24% | 5.081% | 6.606% | 1
2032-33 | 52.4% | 7.166% | 10.53% | 18.9% | 4.327% | 6.671% | 1
2033-34 | 50.47% | 8.354% | 10.59% | 20.44% | 3.561% | 6.584% | 1
2034-35 | 51.56% | 10.02% | 12.16% | 16.22% | 3.061% | 6.975% | 1
2035-36 | 49.33% | 11.08% | 13.27% | 16.94% | 2.425% | 6.955% | 1
2036-37 | 47.18% | 11.94% | 14.37% | 17.67% | 1.904% | 6.93% | 1
2037-38 | 45.06% | 12.69% | 14.55% | 19.45% | 1.441% | 6.804% | 1
2038-39 | 44.53% | 13.92% | 15.25% | 18.37% | 0.9962% | 6.937% | 1
2039-40 | 42.84% | 14.9% | 15.34% | 19.38% | 0.6407% | 6.892% | 1
2040-41 | 41.81% | 15.95% | 16.01% | 19.01% | 0.2611% | 6.958% | 1
2041-42 | 38.96% | 16.24% | 15.86% | 22.28% | -0.04786% | 6.712% | 1
2042-43 | 38.51% | 17.42% | 16.53% | 21.05% | -0.3595% | 6.85% | 1
2043-44 | 37.16% | 18.27% | 16.53% | 21.92% | -0.6822% | 6.805% | 1
2044-45 | 36.11% | 19.18% | 16.62% | 22.3% | -0.9883% | 6.785% | 1
2045-46 | 35.69% | 20.58% | 16.77% | 21.53% | -1.446% | 6.871% | 1
2046-47 | 34.9% | 21.83% | 16.47% | 21.85% | -1.919% | 6.86% | 1
2047-48 | 34.22% | 23.11% | 16.18% | 21.99% | -2.372% | 6.87% | 1
2048-49 | 32.68% | 23.59% | 15.33% | 24.45% | -2.723% | 6.668% | 1
2049-50 | 32.01% | 24.6% | 15.14% | 24.53% | -2.962% | 6.683% | 1
2050-51 | 31.44% | 25.16% | 14.9% | 25.07% | -3.223% | 6.651% | 1
2051-52 | 30.79% | 25.43% | 14.93% | 25.72% | -3.48% | 6.614% | 1

## Demand vs Generation FY
Demand vs Renewable Energy Generation
This sheet contains information relating to the forecast amount of demand and renewable energy generation in SA under the step change scenario over the forecast period.
The renewable data is inclusive of both wind medium and solar amounts. Demand is the operational demand and is inclusive of hydrogen.
Amount (TWh)
FY | Operational Demand | Renewable ISP | FY Ending
2018-19 | 12.2365 | 6.0277 | 2019
2019-20 | 11.9636 | 6.2809 | 2020
2020-21 | 11.616 | 6.4117 | 2021
2021-22 | 11.4475 | 6.8289 | 2022
2022-23 | 11.5063 | 7.4559 | 2023
2023-24 |  |  | 2024
2024-25 | 11.3777 | 10.0842 | 2025
2025-26 | 12.0032 | 10.2825 | 2026
2026-27 | 13.1931 | 10.6281 | 2027
2027-28 | 14.0646 | 11.7859 | 2028
2028-29 | 14.5782 | 11.9148 | 2029
2029-30 | 15.2144 | 14.3818 | 2030
2030-31 | 16.2328 | 14.9789 | 2031
2031-32 | 16.5226 | 16.1169 | 2032
2032-33 | 16.6503 | 16.9977 | 2033
2033-34 | 17.3178 | 18.5268 | 2034
2034-35 | 16.9539 | 17.034 | 2035
2035-36 | 17.7275 | 17.0827 | 2036
2036-37 | 18.5688 | 16.6085 | 2037
2037-38 | 19.5112 | 18.2467 | 2038
2038-39 | 19.653 | 17.8659 | 2039
2039-40 | 20.1787 | 16.3622 | 2040
2040-41 | 20.4246 | 19.1717 | 2041
2041-42 | 21.6657 | 19.529 | 2042
2042-43 | 21.7027 | 20.2358 | 2043
2043-44 | 22.2009 | 20.2262 | 2044
2044-45 | 22.4408 | 24.3498 | 2045
2045-46 | 22.1891 | 28.7779 | 2046
2046-47 | 22.1237 | 29.4164 | 2047
2047-48 | 22.1208 | 30.3557 | 2048
2048-49 | 22.6991 | 29.9083 | 2049
2049-50 | 22.734 | 29.6894 | 2050
2050-51 | 22.7112 | 29.3088 | 2051
2051-52 | 22.6935 | 31.3922 | 2052

## CP Demand vs Generation CY
Demand vs Renewable Energy Generation for the Copper Plate Case (Values Adjusted to Calendar Year)
This sheet contains information relating to the forecast amount of demand and renewable energy generation in SA under the step change scenario over the forecast period when looking at the copper plate model.
The renewable data is inclusive of both wind medium and solar amounts. Demand is the operational demand minus transmission and distribution losses and is inclusive of hydrogen.
Amount (TWh)
Calendar Year | Operational Demand | Renewable | Exceedance
2020 | 11.7898 | #REF!
2021 | 11.5317 | #REF!
2022 | 11.4769 | #REF!
2023 | 11.5063 | #REF!
2024
2025 | 11.7562 | 10.0232 | Not Net Zero
2026 | 12.6964 | 10.5194 | Not Net Zero
2027 | 13.4318 | 11.2691 | Not Net Zero
2028 | 14.6218 | 11.926 | Not Net Zero
2029 | 14.7392 | 13.0409 | Not Net Zero
2030 | 15.8604 | 14.6092 | Not Net Zero
2031 | 16.2232 | 15.4432 | Not Net Zero
2032 | 16.6776 | 16.9619 | 0.28435
2033 | 17.0226 | 18.1112 | 1.0886
2034 | 16.9688 | 17.274 | 0.30523
2035 | 17.5408 | 16.7381 | Not Net Zero
2036 | 18.2531 | 18.0646 | Not Net Zero
2037 | 18.9607 | 16.8856 | Not Net Zero
2038 | 19.6123 | 18.1517 | Not Net Zero
2039 | 19.6836 | 16.6917 | Not Net Zero
2040 | 20.579 | 17.8876 | Not Net Zero
2041 | 20.7322 | 19.4421 | Not Net Zero
2042 | 22.1785 | 19.9568 | Not Net Zero
2043 | 21.5137 | 20.1665 | Not Net Zero
2044 | 22.6705 | 22.1179 | Not Net Zero
2045 | 21.9514 | 26.3455 | 4.3941
2046 | 22.2223 | 29.8056 | 7.5832
2047 | 22.1775 | 30.2838 | 8.1063
2048 | 22.2793 | 29.8269 | 7.5476
2049 | 22.9209 | 29.242 | 6.3211
2050 | 22.9083 | 30.7561 | 7.8478
2051 | 22.4821 | 29.5748 | 7.0927